[image: image1.emf]Whitecroft Lighting Limited   Burlington Street, Ashton - under - Lyne, Lancashire OL7 0AX   Telephone +44 (0)161 330 6811          

 

[image: image2.png]IMPORTANT!

DALI control and DALI
EM coms linked inside

the product

IMPORTANT!

DALI control and DALI
EM coms linked inside
the product





[image: image3.png]. DALIEP | DALIEP
DALI EP DALI EP

|| DALI | DALI
| DALI | DALI
Factory fitted | Neutral Links tobe | | Neutral
links | removed by | |
| Earth installer if | Earth
| Switch Live Se'f-Tetst or| | Switch Live
no
| Perm Live monitored | | Perm Live





[image: image4.png]As supplied
(non fitted

lead
product)

. DALI EP
DAL| EP

| DALI
DALI

Neutral

Earth
Switch Live

Perm Live

WARNING!

CHECK WITH CONTROLS SUPPLIED FOR
CORRECT POSITION OF THE DALI LINKS.
REMOVE THIS LABEL ONCE INSTALLED.





[image: image5.png]As supplied.
Links to
remain if

Self-Test or
non
monitored

| DALIEP
DALI EP

:
|
|

DALI
DALI

Neutral

Earth
Switch Live

Perm Live

As supplied.
Links to
remain if

emg
separately
monitored

| DALIEP
DALI EP

:
|
|

DALI
DALI

Neutral

Earth
Switch Live

Perm Live

Links to be
terminated if

Portal
connected

| DALIEP
DALI EP

!
|
|

. DALI

DALI

Neutral

Earth
Switch Live

Perm Live




[image: image6.png]' | DALIEP
' DAL| EP
—_— - | DALI

Neutral
| Earth
Switch Live

| Perm Live



[image: image7.png]. DALIEP
DALI EP
| DAL
DALI
Neutral

Earth
Switch Live

Perm Live





[image: image8.png]Whitecrof’»)
lighting








EMERGENCY TEST TYPE
	Condition
	Standard 3 Hour (EM)
(Key Switch Tested)
	Self-Test (EP)
(LED Status Monitored)
	Central Test (EP)
(System Monitored)

	On site battery connection needed?
	Yes
	Yes
	Yes

	Allow battery 24 hour charge time?
	Yes
	Yes
	Yes

	Manual discharge needed?
	Yes – Minimum time = 3 hours
If emergency fails initial test, then provide full recharge & reattempt
	No
	No

	Self intelligent automated test
	N/A
	Self commissioning phase charges the battery for 24 hours. 3 hour duration test is then completed, followed by 24 hour recharge. LED indicator signals pass (green) or fail (red)
If luminaire fails initial test, allow full discharge of batteries & repeat 24 hour charge (above)
	Self commissioning phase charges the battery for 24 hours. 3 hour duration test is then completed, followed by 24 hour recharge. LED indicator signals pass (green) or fail (red)
If luminaire fails initial test, allow full discharge of batteries & repeat 24 hour charge (above)

	Central test automation
	N/A
	N/A
	Test schedules can be assigned to complete function & duration tests during appropriate times

	Compliance Reporting of Tests
	On site presence needed

Manual recording of results (BS5266)
	Automated test (site presence not needed)

Periodic inspection of status LED indicator

Manual recording of results (BS5266)
	Scheduled test (site presence not needed)

Periodic inspection for result verfication

Automatic digital record of results (BS5266) 


LED STATUS INDICATOR DEFINITIONS

	LED Indicator Status EP (Colour & Flashing)
	Mackwell
	Tridonic
	Signify
	ELP

	Permanent Green
	System OK, fully charged
	System OK, fully charged
	System OK, fully charged
	System OK, fully charged

	Fast flashing Green
	Functional test underway
	Functional test underway
	Functional test underway
	Functional test underway

	Slow flashing green
	Commissioning/Duration test underway
	Commissioning/Duration test underway
	Commissioning/Duration test underway
	Commissioning/Duration test underway

	10 second green blink
	Standby mode
	N/A
	N/A
	Standby mode

	Double pulsing green
	Inhibit mode
	Inhibit mode
	N/A
	Rest mode



	Permanent red
	N/A
	Lamp fault
	Battery connection abnormal or failure
	N/A

	Fast flashing red
	LED Lamp fault
	Battery/Charging fault
	Battery/Charging fault
	Lamp/LED fault

	Slow flashing red
	Battery/Charging fault
	Battery fault
	Lamp connection Failure
	Battery/Charging fault

	Alternate Green/Red flash
	DALI Addressing Identification Mode
	DALI Addressing Identification Mode
	DALI Addressing Identification Mode
	DALI Addressing Identification

Mode

	Off
	Loss of mains/battery supply
	Loss of mains/battery supply
	Loss of mains/battery supply
	Loss of mains/battery supply


GENERAL INFORMATION





Connection to mains wiring should be carried out by a qualified electrician in accordance with IEE wiring regulations. 


All luminaires apart from Class II luminaires must be earthed


Ensure that the rated luminaire voltage and frequency requirements are compatible with the available mains supply. 


Do not use high voltage insulation testing equipment. Such testing can cause irreparable damage to the electronic components.


Ensure there is a stable permanent supply to the luminaire before connecting the batteries


Ensure the luminaire is isolated before carrying out maintenance


The batteries have a design life of 4 years when installed, conditioned and operated in accordance with this instruction. When the batteries no longer meet their rated duration, they should be replaced


Note: some older chemistry batteries like NiCd and NiMH when changing to LiFePO₄ will also require the inverter to be changed.








BATTERY STORAGE/CARE DETAILS





Optimal storage conditions (when not in service and batteries disconnected) 


LiFePO₄ 0°C to 25°C (6 months onsite maximum)





Battery activation 


For new LiFePO₄ batteries activation of the cell is required to ensure specified design life. 


If the emergency luminaire does not pass the initial 3hr duration test a further full charge and discharge cycle may be required to activate the battery chemistry. 


All Batteries are supplied disconnected





Old batteries must be handled and disposed of by specialist disposal experts. Under no circumstances should they be pierced or incinerated. 


Do not put the luminaire into emergency mode until the batteries are fully charged 








EMERGENCY SUPPLIES





Power to energise emergency luminaires can come from integral batteries within the luminaire (self-contained) or from a remote Central Battery system or Static Inverter. This power supply is intended to energise the emergency circuit within any emergency luminaire upon failure of the normal supply.





Integral battery emergency luminaires indicate ‘batteries are charging’ generally by use of an indicator LED mounted in a visible location on the luminaire. When the indicator LED is solid green, the batteries are charging





Emergency luminaires generally have internal supply connections: Permanent Live (orange), Switched Live (brown), Neutral (blue), and Earth (green/yellow).





All electrical termination and final connections shall be in line with IEE wiring regulations BS7671
































Emergency Luminaire


(EM / EP)














































































































Emergency Luminaire 


Install & Maintenance 


Guide





Emergency


Luminaire


EM/EP











PK_LEAFLETEMGUIDE                                                                        May 2026 - Rev F








          �





DALI LINKS





When a full controls system is being used to provide general lighting control and emergency testing and reporting facility (Organic Response Portal, Whitecroft Connect or third-party system), DALI links will need to be introduced inside light fittings where the driver and emergency inverter is integrated into the same product. This is to provide the system with control of both the driver and emergency inverter.





Please Note: please refer to product specific installation details for information on exact terminations.





FACTORY FITTED LEADS & PLUGS





When a factory fitted lead and plug has been supplied connected to the light fitting as part of the manufacturing process, Whitecroft will terminate the links between DALI and DALI EP (driver and inverter), unless specified otherwise as part of a special project request.





If control and emergency (for general lighting control and emergency monitoring) are being provided by the same system (Organic Response Portal, Whitecroft Connect or third-party system), then the links need to remain in place. If the systems are separate – i.e. general lighting control and emergency are provided by two different systems, the links will need to be removed by the installer.





�


�





STANDARD PRODUCTS (NO FACTORY FITTED LEADS)





Products supplied without factory fitted leads and plugs will not include DALI links, unless specified otherwise as part of a special project request. These will need to be terminated by the installing contractor to match the controls and/or emergency monitoring systems being deployed. The DALI link cables are fixed to the body of the emergency luminaire by a label as shown below:





�         





There may be instances where there is a mix of systems and therefore care must be taken to ensure cable requirements are terminated correctly. Some examples are shown opposite.











Organic Response integrated luminaire with COMEPS connections





When the luminaire is supplied with an integral Organic Response node, the DALI terminals associated with the Organic Response Node have the connections blocked to stop inadvertent connection. If the luminaire is to be used for emergency reporting on the Organic Response Portal, then the terminals should be unblocked and linked to the DALI EP terminals to match the diagram shown below right.





�





Local DALI + DALI Emergency





For applications where the method of lighting control is a local DALI device (such as a DALI Broadcast sensor) and DALI emergency testing and reporting system, two DALI feeds would need to be completed at the light fitting – one to the DALI driver from the DALI device and one to the DALI EP terminals from the emergency monitoring system.





�





DALI Emergency Only





For applications where only a DALI emergency system is being used, the DALI cabling needs to be terminated to the DALI EP terminals.





�





FAULT FINDING





Inspection / fault finding work must be carried out by a suitably electrically qualified person.





Initial checks must include main voltage checks including any circuit protective devices and integrity of internal/external wiring fixed or modular wiring.





Please read BATTERY STORAGE/CARE DETAILS on page 1 before continuing. 





CAUTION: Even if the power supply to the emergency luminaire may be disconnected, there may still be high voltages inside the fitting. Disconnect batteries when maintaining internal wiring.





A.   LED indicator non-operational and does not work in Emergency mode.  


Check that the permanent 230v supply is present in the luminaire.


Check the batteries are properly connected.


Replace the batteries with known working units. 


Replace the inverter ensuring you change it ‘wire for wire’.  


If the luminaire still does not function, Contact Whitecroft Aftercare team. 





B.   Luminaire functions in Emergency mode but will not function in Standard mode.  


Check that the Switched Live is present.  


Check that the Switched and Permanent Supplies are correctly connected.


Check that there is 230v at the ‘Live Out’ terminal of the emergency inverter.  


If the luminaire still does not function, Contact Whitecroft Aftercare team. 





C.   LED indicator illuminated but luminaire does not work in Emergency mode.  


Check light engines in emergency circuit are working


Replace the batteries with known working units.  


Replace the inverter ensuring you change it ‘wire for wire’.  


If the luminaire still does not function, Contact Whitecroft Aftercare team. 





D.   LED indicator not illuminated but luminaire functions in all other respects.  


Check the cable to the LED indicator; make sure it is properly terminated and has not been trapped or cut.  


Replace the LED indicator with a known working one.  


Replace the inverter ensuring you change it ‘wire for wire’.  


If the luminaire still does not function, Contact Whitecroft Aftercare team. 





E.   Luminaire did not last a 3-hour duration test.  


Check that the batteries have been charged for at least 24 to fully charge


Check that the Switched and Permanent Supplies are correctly connected.  


Replace the batteries with known working units. 


Replace the inverter ensuring you change it ‘wire for wire’.


If the luminaire still does not function, Contact Whitecroft Aftercare team.
































TESTING REGIME





 As detailed in BSEN50172 (BS5266-8)


Monthly function test (30s) to check luminaires are functioning correctly (unless detailed differently in commissioning procedure)


Annually full duration test to check the luminaires are functioning correctly and meet their full duration


Emergency testing results must be documented and be available for inspection.





MAIN CAUSES FOR PREMATURE BATTERY FAILURE:





Over cycling of batteries for example caused by an unstable mains supply. Batteries are designed for up to a maximum of 4 full discharges per year. Over cycling will reduce the life expectancy.


Leaving connected batteries in a discharged state (maximum 2 weeks).


Ambient temperatures (when used outside parameters specified by Whitecroft lighting) 


Repeated partial discharging and recharging of batteries (memory effect)





LED STATUS INDICATOR FOR SELF-TEST OR CENTRAL TEST INSTALLATIONS





Whitecroft Lighting Ltd only use reputable control gear within the manufacturing of all Whitecroft products. Below is a table to show the status indicator connected to the emergency control gear within Whitecroft emergency lighting products.





EM = Green Status LED only and will not change even when key switch tested in the event of a failure.





EP Self-Test= Bi Colour (Green / Red) Status LED and if the luminaire fails or passes the test the status colour will be shown and record, please refer to the table below for clarity 





EP Central system Test = Bi Colour (Green / Red) Status LED and if the luminaire fails or passes the test the status colour will be shown and the pass or fail is digitally recorded within the test schedule preformed from the central test system.











